## Slide 1: Case Study on Determining the Design Fire when Installing Sprinkler Systems in Railway Halls
TRANSCOM 2025: 16th International Scientific Conference on Sustainable, Modern and Safe Transport
Alexandra Kardosova1, Jiri Pokorny1, Lenka Brumarova1, Heidi Janeckova1
1 VŠB – Technical University in Ostrava, Ostrava, Czech Republic
introduction |  | 
The determining of design fires when installing fire sprinkler systems (FSS), represents an important task in the design of fire safety measures for train station halls. To ensure proper device function, its design must be based on a correct design fire. | Current methodologies for determining design fires when installing FSS, or when combined with other fire safety devices, are not entirely unambiguous. | The study was conducted with the aim of determining and subsequently verifying a design fire when installing FSS, for the conditions of railway halls.
materials, methods & implementation
The process of defining a design fire scenario for the railway station involved several steps. A fire scenario was created assuming the fire originated from a technical fault in the electrical installation, with no other hazards considered. The fire load was determined based on combustible materials in the hall and the area, set at 3000 m² for 1000 people. The fire load was calculated using standard values (CSN 73 0802 ed. 2, 2023), considering sales booths and seating, resulting in a value of 30 kg/m², with additional values of 60, 90, and 120 kg/m² evaluated. Four design fire scenarios were proposed based on these values, with calculations factoring in sprinkler head distribution, 1.5 m distance from the fire origin, hall clearance of 6 m. Alpert's equations were used to calculate the under-ceiling flow velocity and gas temperature near the sprinkler head, which, along with other factors, allowed for the calculation of the temperature difference. Finally, the heat release rate, Q, was determined using standard formula (CSN 73 0802 ed. 2, 2023).
results
The findings from the initial calculations and the CFAST fire model reveal critical factors that influence fire development and are essential in determining design fires when installing a fire sprinkler system. Key factors include sprinkler head features (head thermal fuse opening temperature determination, reaction time index, and location), building geometry (clearance of the space), and fire dynamics (heat release rate). The sprinkler head response time, ranging from 119 to 225.5 seconds, is influenced by all these factors. However, when considering the maximum heat release rate, only some factors had a significant impact - namely the properties of the sprinkler head and the building geometry. The fire load values had a minimal effect on the heat release rate, which ranged from 581 to 675 kW. It can be assumed that after the sprinkler head activates, the exponential growth of the fire transitions into a constant development phase, and the heat release rate stabilizes or even decreases. This insight can be applied to the design of other fire safety systems, such as smoke and heat exhaust ventilation systems, and in determining fire parameters in the affected space (e.g., temperature fields, structural temperatures). The study also demonstrated that for defined building dimensions and specific sprinkler head characteristics, the response time can be reliably predicted. For example, in train station halls with a 30 kg/m² fire load and a height of 6 meters, the activation time of a sprinkler head with an opening temperature of 68°C can be assumed to be approximately 220 seconds, after which the fire’s exponential development transitions into a constant rate.
conclusion & implementation path
The installation of fire sprinkler systems along with other fire safety devices is a modern and effective way of protecting people and property in train station halls. In order for the sprinklers to function effectively, it is essential to base their design on accurate design fires. The aim of the article was to present a study that determined the design fires when installing FSS in the train hall environment and then verify them with a fire model. To achieve this goal, a fire design scenario was initially created, where the conditions for the origin and development of the fire were defined. Furthermore, a preliminary design fire was determined, within which initial calculations of the design parameters were performed. The results of the study showed that despite the different response times of the sprinkler heads, the heat release rate values ​​showed only minimal differences, regardless of the fire load value. The fire load value therefore does not fundamentally affect the heat release rate value. This finding can be used as a basis for further research into fire dynamics when installing sprinkler fixed fire extinguishing systems.
acknowledgements
This research was funded by the project “Centre of environmental research: Waste management, circular economy and environmetal secutiry”, grant number SP2022/87.